Software USB communication controller

for UPS PowerCom WOW series for model

WOW-300U, WOW-500U, WOW-700U, WOW-850U, WOW-1000U

Developer of software

research-and-production company "MES-s.r.l."

Release 1.0

August, 21, 2008

Revision History

| Ver | Date | Description | Modify by |
| --- | --- | --- | --- |
| 1.0 | 21.08.2008 | New project | MES-s.r.l |

Table of Contents

1.	Introduction	3

2.	POWERCOM UART Communication Protocols for UPS WOW series for models WOW-300U, WOW-500U, WOW-700U, WOW-850U, WOW-1000U	3

3.	Description of the HID Reports for PowerCom UPS-USB interface WOW series	5

4.	Data for Usage from UART of Power Devices PowerCom and constants.	8

5.	Data for calculation of parametres in the table of time RunTimeToEmpty.	13

6.	Conditions for setting  Present Status.	14

7.  Position of SN (serial number) in file of firmware (WOW.hex  or  WOW.rom) – OB17.	15

### Introduction

Software USB communication controller for UPS PowerCom WOW series for model WOW-300U, WOW-500U, WOW-700U, WOW-850U,

WOW-1000U is developed on the basis of POWERCOM UART Communication Protocols for UPS WOW series.

### POWERCOM UART Communication Protocols for UPS WOW series for models WOW-300U, WOW-500U, WOW-700U, WOW-850U, WOW-1000U

Table 1.

******************************************************************************

*  COMM --- UPS AND COMPUTER COMMUNICATION SUBROUTINE                        *

*  FILENAME : COMM.ASM                                                       *

*----------------------------------------------------------------------------*

* BPS = 1200, 1 START BIT, 1 END BIT, 16 DATA BIT                            *

*----------------------------------------------------------------------------*

*  UPS receive 1 byte data is 1: UPS will echo 16 bytes status               *

*      byte  0  is load level                                                *

*      byte  1  is battery level                                             *

*      byte  2  is input voltage             (Volt = b2*2)                   *

*      byte  3  is output voltage            (Volt = b3*2)                   *

*      byte  4  is input frequency                                           *

*      byte  5  is Firmware version          EX: V0.0 = 00                   *

*      byte  6  is output frequency                                          *

*      byte  7  is UPS echo schedule count time high minute byte (0..255)    *

*      byte  8  is UPS echo schedule count time low  minute byte (0..255)    *

*      byte  9  bit 0 is line fail (1 = INV, 0 = LINE)                       *

*               bit 1 is low battery (1 = BAT LOW, 0 = NORMAL)               *

*               bit 2 X                                                      *

*               bit 3 X                                                      *

*               bit 4 X                                                      *

*               bit 5 Load status (1 = OVERLOAD, 0 = NORMAL)                 *

*               bit 6 X                                                      *

*               bit 7 SD mode display                                        *

*      byte  10 bit 0 UPS fault  (1 = FAILT)                                 *

*               bit 1 Bat status (1 = BAD, 0 = NORMAL)                       *

*               bit 2 Test mode  (1 = TEST,0 = NORMAL)                       *

*               bit 3                                                        *

*               bit 4 Pre-SD count mode (1 = ACTIVE)                         *

*               bit 5 Schedule count mode (1 = ACTIVE)                       *

*               bit 6                                                        *

*               bit 7 0                                                      *

*      byte  11 is UPS series name                                           *

WOW=4Fh='O'                                                  *

*      byte  12 is UPS model number and Config Voltage                      	   *

*               300 = 2xH    500 = AxH    700 = CxH                          *

*               850 = ExH   1000 = FxH            		                  *

*               100V = x0H   110V = x1H   115V = x2H   120V = x3H            *

*               200V = x7H   220V = x8H   230V = x9H   240V = xAH            *

*      byte  13 is is UPS echo PRE-SD count time min (0 – 255)               *

*      byte  14 is UPS echo PRE-SD count time sec (0 – 59)                   *

*      byte  15 is DC BUS VOLTAGE      		(Volt = b15*2)              	   *

*  From Byte 0 to Byte 15 use binary data                                    *

*                                                                            *

*  Receive data 3: UPS self test                                             *

*                                                                            *

*  Receive data 4: WAKEUP TIME SETUP,  BYTE 1 IS HIGH BYTE MIN (0-255)       *

*                                      BYTE 2 IS LOW  BYTE MIN (0-255)       *

*                  UPS in sleep mode echo status is all zero                 *

*                  EX: SET WAKEUP TIME 1 HR  4 0 60                          *

*                                                                            *

*  Receive data 11: UPS WAKEUP (?)                                           *

*                                                                            *

*  Receive data 185: ENABLE AC NORMAL RESTART                                *

*  Receive data 186: DISABLE AC NORMAL RESTART                               *

*  Receive data 188: PRE-SD COUNT                                            *

*                   byte 1 is MIN                                            *

*                   byte 2 is SEC                                            *

*  EX: pre-shutdown counter count 1 minute and enable AC normal wakeup  	   *

*           185 188 1 0                                                      *

*********************************************************************************************

### Description of the HID Reports for PowerCom UPS-USB interface WOW series

Table 2.

| Report namber | Page, Usage ID | Usage Name | Data Access |
| --- | --- | --- | --- |
|  | 8404 | UPS COLLECTION (Application) |  |
|  | 8424 | PowerSummary COLLECTION (Logical) |  |
| 1 | 84FE | iProduct | R/O |
| 2 | 84FF | iSerialNumber | R/O |
| 3 | 84FD | iManufacturer | R/O |
| 4 | 858F | iOEMInformation | R/O |
| 5 | 8589 | iDeviceChemistery | R/O |
| 7 | 858B | Rechargable | R/O |
| 8 | 852C | CapacityMode | R/O |
| 9 | 8583 | DesignCapacity * | R/O |
|  | 8567 | FullChargeCapacity * |  |
| 10 | 8566 | RemainingCapacity | R/O |
| 11 | 858C | WarningCapacityLimit | R/O |
| 12 | 8529 | RemainingCapacityLimit | R/O |
| 13 | 8585 | ManufacturerDate | R/O |
| 14 | 8568 | RunTimeToEmpty | R/O |
| 15 | 8457 | DelayBeforeShutdown | R/W |
| 16 | 8456 | DelayBeforeStartup | R/W |
| 17 | 8440 | ConfigVoltage | R/O |
| 18 | 8430 | Voltage | R/O |
| 19 | 845A | AudibleAlarmControl | R/O |
| 20 | 8402 | PresentStatus COLLECTION (Logical) | R/O |
|  |  | Collection multi-bits Report ** |  |
|  | 8544 | Charging |  |
|  | 8545 | Discharging |  |
|  | 85D0 | ACPresent |  |
|  | 85D1 | BatteryPresent |  |
|  | 8542 | BelowRemainingCapacityLimit ** |  |
|  | 8543 | RemainingTimeLimitExpired ** |  |
|  | 854B | NeedReplacement |  |
|  | 85DB | VoltageNotRegulated ** |  |
|  | 8468 | ShutdownRequested ** |  |
|  | 8469 | ShutdownImminent |  |
|  | 8473 | CommunicationLost |  |
|  | 8465 | Overload |  |
|  |  | COUNT (3) ** |  |
|  | 8680 | Usage (80) from Usage_Page (86) ** |  |
|  |  | END_COLLECTION [PresentStatus, Logical] |  |
|  |  | END_COLLECTION [PoweSummary, Logical] |  |
|  | 8412 | Battery COLLECTION (Physical) |  |
| 21 | 8458 | Test | R/W |
| 22 | 8470 | Initialized | W/O |
| 23 | 8585 | ManufacturerDate | R/O |
| 24 | 8566 | RemainingCapacity | R/O |
| 25 | 8440 | ConfigVoltage | R/O |
| 26 | 8430 | Voltage | R/O |
| 27 | 8456 | DelayBeforeStartup | R/W |
|  |  | END_COLLECTION [Battery, Physical] |  |
|  | 841A | Input COLLECTION (Physical) |  |
| 28 | 8440 | ConfigVoltage | R/O |
| 29 | 8430 | Voltage | R/O |
| 30 | 8432 | Frequency | R/O |
|  |  | END_COLLECTION [Input, Physical] |  |
|  | 841C | Output COLLECTION (Physical) |  |
| 31 | 8435 | PercentLoad | R/O |
| 32 | 8440 | ConfigVoltage | R/O |
| 33 | 8430 | Voltage | R/O |
| 34 | 8432 | Frequency | R/O |
| 35 | 8457 | DelayBeforeShutdown | R/W |
| 36 | 8456 | DelayBeforeStartup | R/W |
|  |  | END_COLLECTION [Output, Physical] |  |
|  | 8416 | PowerConverter (Physical) |  |
| 42 | 8430 | Voltage | R/O |
|  |  | END_COLLECTION [PowerConverter, Physical] |  |
| 6 | 8401 | iName | R/O |
| 37 | 845A | Audible Alarm Control | R/O |
| 38 | 8402 | Present Status COLLECTION (Logical) | R/O |
|  |  | Collection multi-bits Report |  |
|  | 8544 | Charging |  |
|  | 8545 | Discharging |  |
|  | 85D0 | ACPresent |  |
|  | 85D1 | BatteryPresent |  |
|  | 8542 | BelowRemainingCapacityLimit ** |  |
|  | 8543 | RemainingTimeLimitExpired ** |  |
|  | 854B | NeedReplacement |  |
|  | 85DB | VoltageNotRegulated ** |  |
|  | 8468 | ShutdownRequested ** |  |
|  | 8469 | ShutdownImminent |  |
|  | 8473 | CommunicationLost |  |
|  | 8465 | Overload |  |
|  | 846E | Boost |  |
|  | 846F | Buck |  |
|  | 8471 | Tested |  |
|  | 8680 | Usage(80) from Usage_Page (86) ** |  |
|  |  | END_COLLECTION [PresentStatus, Logical] |  |
| 39 | 8469 | ShutdownImminent | R/W |
| 40 | 842F | User defined data | R/W |
|  |  | END_COLLECTION [UPS, Application] |  |

*)   - Two Usage in one report.

**) - Not to use. For compatibility with system (APC-based) driver.

### Data for Usage from UART of Power Devices PowerCom and constants.

Table 3. System requests for usage with Microsoft UPS system driver (first Byte is Byte 0 )

| Report number | Page, Usage ID | Usage Name | Data Access | Data | Length |
| --- | --- | --- | --- | --- | --- |
|  | 8424 | PowerSummary COLLECTION |  |  |  |
| 1 | 84FE | iProduct | R/O | UPS WOW-ХХХХU FW3.A4.01 ХХХХ - Model name from Table 4 | 56 Byte |
| 2 | 84FF | iSerialNumber | R/O | 0A2-0000-0001 | 32 Byte |
| 3 | 84FD | iManufacturer | R/O | POWERCOM Co.,LTD | 34 Byte |
| 4 | 858F | iOEMInformation | R/O | POWERCOM Co.,LTD | 34 Byte |
| 5 | 8589 | iDeviceChemistery | R/O | PbAc | 10 Byte |
| 7 | 858B | Rechargable | R/O | 1 | 1 Byte |
| 8 | 852C | CapacityMode | R/O | 2 (%) | 1 Byte |
| 9 | 8583 | Designcapacity* | R/O | 100 (in %) | 2 Byte |
|  | 8567 | FullChargeCapacity * |  | 100 (in %) |  |
| 10 | 8566 | RemainingCapacity | R/O | Byte 1 "battery level" (in %) | 1 Byte |
| 11 | 858C | WarningCapacityLimit | R/O | 30 (in %) | 1 Byte |
| 12 | 8529 | RemainingCapacityLimit | R/O | Initially 10 (in %), is it hereinafter assigned by system driver | 1 Byte |
| 13 | 8585 | ManufacturerDate | R/O | ( Year-1980 ) * 512 + Month * 32 + Day | 2 Byte |
| 14 | 8568 | RunTimeToEmpty | R/O | It Is Calculated on the grounds of Byte 0, Byte 1, Byte 12, ( in sec ) Calculated in table T =( ( Caccum * K * BatteryLevel * 60 min ) / ( Pnom * LoadLevel ) ) * 60 Where K =4,8 for WOW-300 K =9,6 for WOW-500….WOW-1000 Unit Caccum – 2%, Unit LoadLevel – 16%, | 2 Byte |
| 15 | 8457 | DelayBeforeShutdown *** | R/W | Read: Byte 13, Byte 14 (min, sec) Write: Two free senior bits of byte of seconds are used for possibility of a choice of a prefix-command before 188 command performance If Byte(sec), bit7=0 and bit6=0 Then If Byte 9, bit0=1 Then command 185, 188, min, sec If Byte 9, bit0=0 Then command 186, 188, min, sec If Byte(sec), bit7=0 and bit6=1 Then command 185, 188, min, sec If Byte(sec), bit7=1 and bit6=0 Then command 186, 188, min, sec If Byte(sec), bit7=1 and bit6=1 Then command 188, min, sec | 2 Byte |
| 16 | 8456 | DelayBeforeStartup *** | R/W | Read: Byte 7, Byte 8 (min) Write: Command 4, high byte min, low byte min | 2 Byte |
| 17 | 8440 | ConfigVoltage | R/O | from Byte 12 (see table 3) | 1 Byte |
| 18 | 8430 | Voltage | R/O | (Byte 3)*2 "output Voltage" | 2 Byte |
| 19 | 845A | AudibleAlarmControl | R/O | If Byte 10, bit3=1 Then value =2 If Byte 10, bit3=0 Then value =1 | 1 Byte |
|  | 8402 | Present Status COLLECTION |  |  |  |
| 20 |  | Collection multi-bits Report | R/O |  | 2 Byte |
|  | 8544 | Charging |  | (see table 4) |  |
|  | 8545 | Discharging |  | (see table 4) |  |
|  | 85D0 | ACPresent |  | Byte 9, Not bit0 |  |
|  | 85D1 | BatteryPresent |  | (see table 4) |  |
|  | 8542 | BelowRemainingCapacityLimit ** |  | (see table 4) |  |
|  | 8543 | RemainingTimeLimitExpired ** |  | (see table 4) |  |
|  | 854B | NeedReplacement |  | (see table 4) |  |
|  | 85DB | VoltageNotRegulated |  | Byte 10, bit0 |  |
|  | 8468 | ShutdownRequested ** |  | 0 |  |
|  | 8469 | ShutdownImminent |  | IF [Byte 10, bit6=0] and [Byte 9, bit0=1] and [Byte 0=0] Then value =1 Else value = 0 |  |
|  | 8473 | CommunicationLost |  | IF Error UART Then value =1 |  |
|  | 8465 | Overload |  | Byte 9, bit5 |  |
|  | 846E | COUNT(3)** |  |  |  |
|  | 8680 | Usage(80) from Usage_Page (86) |  | Constant, value=0 |  |
|  | 8412 | Battery COLLECTION |  |  |  |
| 21 | 8458 | Test | R/W | Read: If Byte 10 bit1=0 AND bit2=0 Then value = 1 (“Done and Passed”) If Byte 10 bit1 =1 AND bit2=0 Then value = 3 (“Done and Error”) If Byte 10 bit2 =1 Then value = 5 (“Test in progress”) Write : If value =1 Then command 3 , Else No_command | 1 Byte |
| 22 | 8470 | Initialized | W/O | Write : If value =1 Then command 11 , Else No_command | 1 Byte |
| 23 | 8585 | ManufacturerDate | R/O | ( Year-1980 ) * 512 + Month * 32 + Day | 2 Byte |
| 24 | 8566 | RemainingCapacity | R/O | Byte 1 " battery level " (in %) | 1 Byte |
| 25 | 8440 | ConfigVoltage | R/O | (see Report number 17) | 1 Byte |
| 26 | 8430 | Voltage | R/O | (see Report number 18) | 2 Byte |
| 27 | 8456 | DelayBeforeStartup *** | R/W | (see Report number 16) | 2 Byte |
|  | 841A | Input COLLECTION |  |  |  |
| 28 | 8440 | ConfigVoltage | R/O | (see Report number 17) | 1 Byte |
| 29 | 8430 | Voltage | R/O | (Byte 2)*2 "input Voltage" (in Volt) | 2 Byte |
| 30 | 8432 | Frequency | R/O | Byte 4 "input Frequency" (in Hz) | 1 Byte |
|  | 841C | Output COLLECTION |  |  |  |
| 31 | 8435 | PercentLoad | R/O | Byte 0 "load level" (in %) | 1 Byte |
| 32 | 8440 | ConfigVoltage | R/O | (see Report number 17) | 1 Byte |
| 33 | 8430 | Voltage | R/O | (Byte 3)*2 "output Voltage" (in Volt) | 2 Byte |
| 34 | 8432 | Frequency | R/O | Byte 6 "output Frequency" (in Hz) | 1 Byte |
| 35 | 8457 | DelayBeforeShutdown *** | R/W | (see Report number 15) | 2 Byte |
| 36 | 8456 | DelayBeforeStartup *** | R/W | (see Report number 16) | 2 Byte |
|  | 8416 | PowerConverter COLLECTION |  |  |  |
| 42 | 8430 | Voltage | R/O | (Byte 15)*2 "DC Bus Voltage" | 2 Byte |
| 6 | 8401 | iName | R/O | POWERCOM USB UPS | 32 Byte |
| 37 | 845A | Audible Alarm Control | R/O | (see Report number 19) | 1 Byte |
|  | 8402 | Present Status COLLECTION |  |  |  |
| 38 |  | Collection multi-bits Report | R/O |  | 2 Byte |
|  | 8544 | Charging |  | (see Report number 20) |  |
|  | 8545 | Discharging |  | (see Report number 20) |  |
|  | 85D0 | ACPresent |  | (see Report number 20) |  |
|  | 85D1 | BatteryPresent |  | (see Report number 20) |  |
|  | 8542 | BelowRemainingCapacityLimit ** |  | (see Report number 20) |  |
|  | 8543 | RemainingTimeLimitExpired ** |  | (see Report number 20) |  |
|  | 854B | NeedReplacement |  | (see Report number 20) |  |
|  | 85DB | VoltageNotRegulated |  | (see Report number 20) |  |
|  | 8468 | ShutdownRequested ** |  | (see Report number 20) |  |
|  | 8469 | ShutdownImminent |  | (see Report number 20) |  |
|  | 8473 | CommunicationLost |  | (see Report number 20) |  |
|  | 8465 | Overload |  | (see Report number 20) |  |
|  | 846E | Boost |  | 0 |  |
|  | 846F | Buck |  | 0 |  |
|  | 8471 | Tested |  | Byte 10, bit2 |  |
| 39 | 8469 | ShutdownImminent | R/W | Read: IF [Byte 10, bit6=0] Then value = 1 Else value = 0 Write: IF value=1 Then command “G” Else command “g” | 1 Byte |
| 40 | 842F | User defined data | R/W | Read: Byte 1: Roll-overed UPS polling counter (0..255,0…) Byte 2: UPS polling status byte Bytes 3..18: 16 bytes status from UPS Write: up to 7 bytes data to UPS | 18 Byte 7 Byte |

*)         - Two Usage in one report.

**)       - Not to use. For compatibility with system (APC-based) driver.

***)     - Does not correspond to the standard "Universal Serial Bus Usage Tables for HID Power Devices".

Productivity microcontroller CY7C63723 is not sufficient, that real-time to execute transformations data.

### Data for calculation of parametres in the table of time RunTimeToEmpty.

Table 4.

Higher part of the byte 12  - UPS model, Pnom and Design Capacity

| Higher part of the byte 12 | UPS_Model | Pnom (Wt) | DesignCapacity (A/H) | Number Acc. | Efficiency Inverter (%) |
| --- | --- | --- | --- | --- | --- |
| 2 | WOW-300 | 165W | 6V 5AH | 1 | 75~85% |
| A | WOW-500 | 250W | 12V 3.3AH | 1 | 75~85% |
| C | WOW-700 | 350W | 12V 4AH | 1 | 75~85% |
| E | WOW-850 | 425W | 12V 7AH | 1 | 75~85% |
| F | WOW-1000 | 500W | 12V 9AH | 1 | 75~85% |

Lower part of the byte 12 - Config Voltage.

| lower part of the byte | ConfigVoltage (Volt) |
| --- | --- |
| 0 | 100 |
| 1 | 110 |
| 2 | 115 |
| 3 | 120 |
| 7 | 200 |
| 8 | 220 |
| 9 | 230 |
| A | 240 |

### Conditions for setting  Present Status.

Table 5.

|  |  | HEX | USAGE (80) | Tested | Buck | Boost | Overload | Communi- cation Lost | Shutdown Imminent | Shutdown Requested | VoltageNot Regulated | Need Replacement | Remaining Time Limit Expired | Below Remaining CapacityLimit | Battery Present | ACPresent | Discharging | Charging |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 |
|  | Fully Charged BatteryLeve l= 100% |  | 0 | T* | 0 | 0 | T* | T* | 0 | 0 | T* | 0 | 0 | 0 | 1 | 1 | 0 | 0 |
|  | Discharging 20% ( BatteryLevel ( 100% |  | 0 | T* | 0 | 0 | T* | T* | 0 | 0 | T* | 0 | 0 | 0 | 1 | 0 | 1 | 0 |
|  | Discharging 0% < BatteryLevel ( 20% |  | 0 | T* | 0 | 0 | T* | T* | 0 | 0 | T* | 0 | 1 | 0 | 1 | 0 | 1 | 0 |
|  | Fully Discharged BatteryLevel = 0% Battery Low = 0 |  | 0 | T* | 0 | 0 | T* | T* | 0 | 0 | T* | 0 | 1 | 1 | 1 | 0 | 1 | 0 |
|  | Fully Discharged BatteryLevel = 0% Battery Low = 1 |  | 0 | T* | 0 | 0 | T* | T* | 1 | 0 | T* | 1 | 1 | 1 | 1 | 0 | 0 | 0 |
|  | Charging BatteryLevel = 0% Battery Low = 1 |  | 0 | T* | 0 | 0 | T* | T* | 0 | 0 | T* | 1 | 1 | 1 | 1 | 1 | 0 | 1 |
|  | Charging BatteryLevel = 0% Battery Low = 0 |  | 0 | T* | 0 | 0 | T* | T* | 0 | 0 | T* | 0 | 1 | 1 | 1 | 1 | 0 | 1 |
|  | Charging 0% < BatteryLevel ( 20% |  | 0 | T* | 0 | 0 | T* | T* | 0 | 0 | T* | 0 | 1 | 0 | 1 | 1 | 0 | 1 |
|  | Charging 7% < BatteryLevel ( 99% |  | 0 | T* | 0 | 0 | T* | T* | 0 | 0 | T* | 0 | 0 | 0 | 1 | 1 | 0 | 1 |

T* - with Data from table 4.

### 7.  Position of SN (serial number) in file of firmware (WOW.hex  or  WOW.rom) – OB17.

Fragment of listing below:

0B15                     iserialnumber_string:                 ; Serial Number String

0B15 20    [00]     db  imanufacturer_string-iserialnumber_string

0B16 03    [00]     db  3

0B17 30 00 ...      dsu "0A4-0000-0001  "

41 00 34 00 2D 00 30 00 30 00 30 00 30 00 2D 00 30 00 30 00 30 00 31 00 20 00 20 00